PUMP PERFORMANCE

Total Dynamic Head

= discharge pressure

= suction pressure

Hydraulic Horsepower

Shaft Efficiency

= theoretical required power (hp)

= actual shaft work or brake-horsepower

note  because there are friction losses inside the pump.

Available Net Positive Suction Head

= suction pressure

= vapor pressure of fluid

NPSHA has to be positive.  Otherwise, the fluid enters the pump with bubbles.

As pressure increases inside the pump the bubbles collapse.

This phenomena is called CAVITATION and it

-Reduces capacity

-Damages the pump

Net Required Positive Suction Head (NPHSR)

Ideal pumps will not cavitate if NPHSA is positive.

However a small pressure decrease can take place in a pump due to internal losses close to the suction.

====>  if NPSHA = 0   bubbles can form and cavitation takes place.

====>  NPSHA is a required value suggested by the manufacturer

SPECIFICATION CRITERIA

NPHSA   >   NPHSR

Head Capacity Curves

Thus,  centrifugal pumps are chosen because

They can operate in a wider range of flowrates which is good for control 			and process flexibility.

---------------------------------------------------------------------------------------------------------

If you are stuck with a positive displacement pump, the following diagram shows how you can regulate flow.

However, this arrangement will:

- use more energy

- heat up fluid

Centrifugal Pump Performance Curves

(Fixed speed, rpm)

Specifying A Pump

1) Need

System head      H5 = (P4-P3)+(P2-P1)

Pump head        Hp

But					 Hp = Hs

Effect of a throttling valve

Since   Hs =  Hp ,  pick the Hs curve close to 80%  open, at maximum flow

Parameters you can control when selecting the pump

- impeller diameter

- speed (not very common)

- the model

Things to look for

- Maximum efficiency

- NPHSA > NPHSR

What to do if NPHSA is too low

NPHSA = P2-PV

Increase P2 !!!     (How?)

Increase Z1

This is the reason why pumping fluids that are close to saturated conditions require that the vessel upstream be elevated. Flash tanks are typical examples of this.

Control Valves

(see Chem. Eng., April 1978, October, 1971)

Valve characteristics

Valve flow Coefficient (Cv)

Q = flowrate (gpm)

= Pressure drop (psi)

( = Specific gravity of fluid

How is Cv measured ?

Measure the flowrate of water at 60 oF where

*   (P = 1 psi

*   valve is totally open

How does the valve behave within a system ?

Let  	(P1 = P2 - P1

(P2 = (P4-P3) - (PV

Valve Pressure Drop Ratio

Effect of valve travel

Installed Characteristics

Valve Specification

Need to give

-  CV

-  Characteristics

HOW TO OBTAIN CV

CV is obtained from flowrate, sp. gr. and (PV at maximum flowrate conditions.

Now look for a valve that has this Cv

Characteristics.

Want linear response when installed since the stem moves linearly with signal coming from controller.

*Large flowrate variation expected

====>  Pick equal %  valve with PR ( 0 at maximum flow conditions.

*Low flowrate variations can pick equal % or linear

Linear is preferred when pump curve is flat.

OPTIMAL PIPE DIAMETER

(P&T ch. 11)

Pumping cost = Annualized cost of pump + Cost of electrcity

Piping costs = C(diameter)n

(includes fittings)

Optimal piping + Pump arrangement

Since Isometric is fixed, then pipe length is fixed and Le (equivalent legth due to fittings and valves) is fixed

Pumping Costs

CE  =  KWR  =  KW/(

(  =  pump efficiency

Recall that

(Pp  =  Discharge pressure - Suction pressure

G  =  Mass flowrate

But

=  System pressure drop

=  Valve pressure drop

Assume that   ( ==>  (  does not change and suction piping has same diameter as discharge piping.)

Now

Then :

Put all together

This is slightly different from P&T, where PR is not considered

use

but

In this way, we have CE as a function of D only!!!!!

Fixed Charges

Total cost

We have to find the minimum of the above total cost funtion. Options are:

1) Calculate for different diameters and determine the lowest one.

2) Use excel solver.

3) In provision, use strategy outlined in 1) in a calculator.

CAVITATION

Cavitation takes place when pressure inside the valve drops below vapor pressure of fluid.

How can that happen ?

Pressure gradient across the valve

Criteria to determine possible cavitation

If	no cavitation

PV   =  Vapor pressure

PC =  Critical pressure

(for PV   <  0.5 P1)

Cf  = 0.98 	equal % flow to open (against stem)

Cf  = 0.85 	equal % flow to close

Sizing Pressure Relief Valves

(Chem. Eng, Feb 1977)

Spring settings

Overpressure for fully open valve

PF  =  1.25 PS

Set pressure  =  PS  =  1.1 PM		(valve starts to open)

Max. Normal operating pressure  =  PM

Sizing :  Need to determine the flowrate at overpressure.  This is related to how fast you want pressure to go down.  Once the flowrate at overpressure is known you specify the area of the orifice

Let	QF  =  flowrate at overpressure

for liquids use bernoulli equation with density (() constant

Velocity in Vessel (VV) ( 0

Q  =  VdA

How to determine Q?

Liquid is in the vessel and will have to release some liquid to reduce pressure.

Recall from Thermodynamics that

But 	(  =  volume expansivity

K  =  isothermal compressibility

In a valve

initial mass

Volume of vessel

W  =  mass to release

But

assume		 Q(t)  =  QF

W  =  (tQFt

t = time in which you want pressure to go down

Gas and Vapor Services

M  =  Molecular weitht

C is a function of

K  =  manufacturer coeficient  (range about 0.95-1.0)

Kb  =  backpressure sizing factor

| Pb/Ps | Kb |
| --- | --- |
| 0.55 | 1 |
| 0.6 | 0.995 |
| 0.7 | 0.945 |
| 0.8 | 0.845 |

The above formula corresponds to the maximum possible velocity through an orifice :  the velocity of sound in the fluid and is borrowed from compressible gas flow theory.

LETDOWN VALVES

Gas letdown

flow rate

inlet pressure (psia)

density (lb/ft3)

high (P will cause choke flow

Liquid letdown  (Vaporization wil cause choke flow)

=  pressure at vena-contracta

high (P will cause choke flow

FL =  Manufacturer constant (0.8-1.0)